# Area valve service unit - Zoning, closure and non-interchangeable screw thread (NIST) tests - Form A4

| Healthcare organisation/ facility: | enter text | Date: | enter a date | Project ref: | enter text |
| --- | --- | --- | --- | --- | --- |

Area/ department/ room: enter text

## Valve zoning, NIST specificity and function

| Service | Gauge no. | Valve no. | Quantity of terminal units | Valve zoning pass/ fail | NIST specificity pass/ fail | NIST function pass/ fail | Comments |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Oxygen | enter text | enter text | enter text | pass/ fail | pass/ fail | pass/ fail | enter text |
| Nitrous oxide | enter text | enter text | enter text | pass/ fail | pass/ fail | pass/ fail | enter text |
| Nitrous oxide/oxygen (50% v/v) mixture | enter text | enter text | enter text | pass/ fail | pass/ fail | pass/ fail | enter text |
| Medical air 4 bar | enter text | enter text | enter text | pass/ fail | pass/ fail | pass/ fail | enter text |
| Surgical air 7 bar | enter text | enter text | enter text | pass/ fail | pass/ fail | pass/ fail | enter text |
| Medical vacuum | enter text | enter text | enter text | pass/ fail | pass/ fail | N/A | enter text |

## Valve tightness

| Service | Gauge no. | Valve no. | Quantity of terminal units | Start pressure (kilo Pascal (kPa)) | Start time | Finish pressure (kPa) | Finish time | Pass/ fail | Comments |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Oxygen | enter text | enter text | enter text | enter text | enter text | enter text | enter text | pass/ fail | enter text |
| Nitrous oxide | enter text | enter text | enter text | enter text | enter text | enter text | enter text | pass/ fail | enter text |
| Nitrous oxide/oxygen (50% v/v) mixture | enter text | enter text | enter text | enter text | enter text | enter text | enter text | pass/ fail | enter text |
| Medical air 4 bar | enter text | enter text | enter text | enter text | enter text | enter text | enter text | pass/ fail | enter text |
| Surgical air 7 bar | enter text | enter text | enter text | enter text | enter text | enter text | enter text | pass/ fail | enter text |
| Medical vacuum | enter text | enter text | enter text | enter text | enter text | enter text | enter text | pass/ fail | enter text |

Notes:

- Pressure differential between upstream (working pressure) and downstream (approximately 300 kPa).

- Medical vacuum systems to be; on vacuum system plant side at distribution pressure and on terminal unit side at approximately 15 kPa (112 millimetres of mercury (mmHg)).

- Test should be conducted over a period of 15 minutes with no change in pressure.

- Ensure that the gas specific probes fully engage into the relevant gas specific NIST and that the probe can be secured.

- Ensure that the NIST allows flow of gas.

- Ensure that the NIST non-return valve (NRV) resets (with the exception of medical vacuum) to prevent flow of gas. In some instances a residual flow will occur, this depends on effective the NIST NRV is.

## Sign off

This is to certify that the above tests have been carried out:

| Test undertaken by: | Name: | enter text | Signature: | enter text | Date: | enter a date |
| --- | --- | --- | --- | --- | --- | --- |
| Test witnessed by: | Name: | enter text | Signature: | enter text | Date: | enter a date |