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SHTM 02-01 Part A.03 - Form A3


2nd fix pressure test and vacuum leakage test - Form A3
	Healthcare organisation/ facility:
	enter text	Date:
	enter a date	Project ref:
	enter text

Pipeline pressure test
	Service
	Gauge 
no.
	Test start pressure (kilo Pascal kPa))
	Test start
date
	Test start time
	Test start temp 
(ºC)
	Test finish pressure (kPa)
	Test finish 
date
	Test finish time
	Test finish temp 
(ºC)
	Pressure drop (ΔP) (kPa)
	[bookmark: Text28]Pass/ fail
comments

	Oxygen
	enter text	enter text	enter a date	enter text	enter text	enter text	enter a date	enter text	enter text	enter text	enter text
	Nitrous oxide
	enter text	enter text	enter a date	enter text	enter text	enter text	enter a date	enter text	enter text	enter text	enter text
	Nitrous oxide/
oxygen (50% v/v) mixture
	enter text	enter text	enter a date	enter text	enter text	enter text	enter a date	enter text	enter text	enter text	enter text
	Medical air 4 bar
	enter text	enter text	enter a date	enter text	enter text	enter text	enter a date	enter text	enter text	enter text	enter text
	Surgical air 7 bar
	enter text	enter text	enter a date	enter text	enter text	enter text	enter a date	enter text	enter text	enter text	enter text


Vacuum leakage test
	Service
	Gauge 
no.
	Test start pressure (kPa)
	Test start
date
	Test start time
	Test start temp 
(ºC)
	Test finish pressure (kPa)
	Test finish 
date
	Test finish time
	Test finish temp 
(ºC)
	Pressure drop (ΔP) (kPa)
	Pass/ fail
comments

	Medical vacuum
	enter text	enter text	enter a date	enter text	enter text	enter text	enter a date	enter text	enter text	enter text	enter text


Test pressure, pressure drop and timescale
	Service
	Test Pressure
	Pressure Drop (max)
	Timescale

	Oxygen
	4 bar/ 400 kPa
	0.2 kPa
	1 hour

	Nitrous oxide
	4 bar/ 400 kPa
	0.2 kPa
	1 hour

	Nitrous oxide/oxygen (50% v/v) mixture
	4 bar/ 400 kPa
	0.2 kPa
	1 hour

	Medical air 4 bar
	4 bar/ 400 kPa
	0.2 kPa
	1 hour

	Surgical air 7 bar
	7 bar/ 700 kPa
	0.5 kPa
	1 hour

	Surgical air 9 bar
	9 bar/ 900 kPa
	0.5 kPa
	1 hour

	Medical vacuum
	450 - 700 millimetres of mercury (mmHg)
	1 kPa/ 7.5 mmHg
	1 hour



	Comments: enter text



Sign off
This is to certify that the above tests have been carried out:
	Test undertaken by:
	Name:
	enter text	Signature:
	enter text	Date:
	tap to enter a date
	Test witnessed by:
	Name:
	enter text	Signature:
	enter text	Date:
	tap to enter a date
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