# 2nd fix pressure test and vacuum leakage test - Form A3

| Healthcare organisation/ facility: | enter text | Date: | enter a date | Project ref: | enter text |
| --- | --- | --- | --- | --- | --- |

## Pipeline pressure test

| Service | Gauge no. | Test start pressure (kilo Pascal kPa)) | Test start date | Test start time | Test start temp (ºC) | Test finish pressure (kPa) | Test finish date | Test finish time | Test finish temp (ºC) | Pressure drop (ΔP) (kPa) | Pass/ fail comments |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Oxygen | enter text | enter text | enter a date | enter text | enter text | enter text | enter a date | enter text | enter text | enter text | enter text |
| Nitrous oxide | enter text | enter text | enter a date | enter text | enter text | enter text | enter a date | enter text | enter text | enter text | enter text |
| Nitrous oxide/ oxygen (50% v/v) mixture | enter text | enter text | enter a date | enter text | enter text | enter text | enter a date | enter text | enter text | enter text | enter text |
| Medical air 4 bar | enter text | enter text | enter a date | enter text | enter text | enter text | enter a date | enter text | enter text | enter text | enter text |
| Surgical air 7 bar | enter text | enter text | enter a date | enter text | enter text | enter text | enter a date | enter text | enter text | enter text | enter text |

## Vacuum leakage test

| Service | Gauge no. | Test start pressure (kPa) | Test start date | Test start time | Test start temp (ºC) | Test finish pressure (kPa) | Test finish date | Test finish time | Test finish temp (ºC) | Pressure drop (ΔP) (kPa) | Pass/ fail comments |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Medical vacuum | enter text | enter text | enter a date | enter text | enter text | enter text | enter a date | enter text | enter text | enter text | enter text |

### Test pressure, pressure drop and timescale

| Service | Test Pressure | Pressure Drop (max) | Timescale |
| --- | --- | --- | --- |
| Oxygen | 4 bar/ 400 kPa | 0.2 kPa | 1 hour |
| Nitrous oxide | 4 bar/ 400 kPa | 0.2 kPa | 1 hour |
| Nitrous oxide/oxygen (50% v/v) mixture | 4 bar/ 400 kPa | 0.2 kPa | 1 hour |
| Medical air 4 bar | 4 bar/ 400 kPa | 0.2 kPa | 1 hour |
| Surgical air 7 bar | 7 bar/ 700 kPa | 0.5 kPa | 1 hour |
| Surgical air 9 bar | 9 bar/ 900 kPa | 0.5 kPa | 1 hour |
| Medical vacuum | 450 - 700 millimetres of mercury (mmHg) | 1 kPa/ 7.5 mmHg | 1 hour |

Comments: enter text

## Sign off

This is to certify that the above tests have been carried out:

| Test undertaken by: | Name: | enter text | Signature: | enter text | Date: | tap to enter a date |
| --- | --- | --- | --- | --- | --- | --- |
| Test witnessed by: | Name: | enter text | Signature: | enter text | Date: | tap to enter a date |