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SHTM 02-01 Part A.02 - Form A2


Carcass - 1st fix pressure, labelling/ marking, sleeving/ supports and cross-connection - Form A2
	Healthcare organisation/ facility:
	enter text	Date:
	enter a date	Project ref:
	enter text

Part 1
Leakage
	Service
	Gauge 
no./ 
leak detection fluid test (LDFT)#
	Test start pressure (kilo Pascal kPa))
	Test start
date
	Test start time
	Test start temp 
(ºC)
	Test finish pressure (kPa)
	Test finish 
date
	Test finish time
	Test finish temp 
(ºC)
	Pressure drop (ΔP) (kPa)
	Pass/ fail comments

	Oxygen
	enter text	enter text	enter a date	enter text	enter text	enter text	enter a date	enter text	enter text	enter text	enter text
	Nitrous oxide
	enter text	enter text	enter a date	enter text	enter text	enter text	enter a date	enter text	enter text	enter text	enter text
	Nitrous oxide/
oxygen (50% v/v) mixture
	enter text	enter text	enter a date	enter text	enter text	enter text	enter a date	enter text	enter text	enter text	enter text
	Medical air 4 bar
	enter text	enter text	enter a date	enter text	enter text	enter text	enter a date	enter text	enter text	enter text	enter text
	Surgical air 7 bar
	enter text	enter text	enter a date	enter text	enter text	enter text	enter a date	enter text	enter text	enter text	enter text
	Medical vacuum*
	enter text	enter text	enter a date	enter text	enter text	enter text	enter a date	enter text	enter text	enter text	enter text
	AGSS
	enter text	enter text	enter a date	enter text	enter text	enter text	enter a date	enter text	enter text	enter text	enter text

* For plastic pipeline systems a pressure of 1.5 bar/ 150 kPa should be set. 
# Delete as appropriate.
If an LDFT test is used then there is no requirement to complete the rest of the table.
Test pressure, pressure drop and timescale
	Service
	Test Pressure
	Pressure Drop (max)
	Timescale

	Oxygen
	10 bar/ 1,000 kPa
	0.2 kPa
	1 hour

	Nitrous oxide
	10 bar/ 1,000 kPa
	0.2 kPa
	1 hour

	Oxygen/nitrous oxide (50% v/v)
	10 bar/ 1,000 kPa
	0.2 kPa
	1 hour

	Medical air 4 bar
	10 bar/ 1,000 kPa
	0.2 kPa
	1 hour

	Surgical air 7 bar
	18 bar/ 1,800 kPa
	0.5 kPa
	1 hour

	Surgical air 9 bar
	18 bar/ 1,800 kPa
	0.5 kPa
	1 hour

	Medical vacuum
	5 bar/ 500 kPa
	0.2 kPa
	1 hour

	Anaesthetic gas scavenging system (AGSS)
	70 kPa
	1 kPa
	15 mins



Labelling and marking, sleeving, supports and cross-connections
	Service
	Labelling and markings
	Sleeving and supports
	Cross-connection test
	Pass/ fail
comments

	Oxygen
	enter text	enter text	enter text	enter text
	Nitrous oxide
	enter text	enter text	enter text	enter text
	Nitrous oxide/oxygen (50% v/v) mixture
	enter text	enter text	enter text	enter text
	Medical air 4 bar
	enter text	enter text	enter text	enter text
	Surgical air 7 bar
	enter text	enter text	enter text	enter text
	Medical vacuum*
	enter text	enter text	enter text	enter text
	AGSS
	enter text	enter text	enter text	enter text


	Comments: enter text



Part 2
	The following pipeline systems interconnections have been made to facilitate the pipeline tests indicated in Part 1:
enter text


Part 3
	The following pipeline systems interconnections have been removed as indicated in Part 2: 
enter text


Sign off
This is to certify that the above tests have been carried out:
	Test undertaken by:
	Name:
	enter text	Signature:
	enter text	Date:
	enter a date
	Test witnessed by:
	Name:
	enter text	Signature:
	enter text	Date:
	enter a date
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