# Carcass - 1st fix pressure, labelling/ marking, sleeving/ supports and cross-connection - Form A2

| Healthcare organisation/ facility: | enter text | Date: | enter a date | Project ref: | enter text |
| --- | --- | --- | --- | --- | --- |

## Part 1

### Leakage

| Service | Gauge no./ leak detection fluid test (LDFT)# | Test start pressure (kilo Pascal kPa)) | Test start date | Test start time | Test start temp (ºC) | Test finish pressure (kPa) | Test finish date | Test finish time | Test finish temp (ºC) | Pressure drop (ΔP) (kPa) | Pass/ fail comments |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Oxygen | enter text | enter text | enter a date | enter text | enter text | enter text | enter a date | enter text | enter text | enter text | enter text |
| Nitrous oxide | enter text | enter text | enter a date | enter text | enter text | enter text | enter a date | enter text | enter text | enter text | enter text |
| Nitrous oxide/ oxygen (50% v/v) mixture | enter text | enter text | enter a date | enter text | enter text | enter text | enter a date | enter text | enter text | enter text | enter text |
| Medical air 4 bar | enter text | enter text | enter a date | enter text | enter text | enter text | enter a date | enter text | enter text | enter text | enter text |
| Surgical air 7 bar | enter text | enter text | enter a date | enter text | enter text | enter text | enter a date | enter text | enter text | enter text | enter text |
| Medical vacuum* | enter text | enter text | enter a date | enter text | enter text | enter text | enter a date | enter text | enter text | enter text | enter text |
| AGSS | enter text | enter text | enter a date | enter text | enter text | enter text | enter a date | enter text | enter text | enter text | enter text |

* For plastic pipeline systems a pressure of 1.5 bar/ 150 kPa should be set.

# Delete as appropriate.

If an LDFT test is used then there is no requirement to complete the rest of the table.

### Test pressure, pressure drop and timescale

| Service | Test Pressure | Pressure Drop (max) | Timescale |
| --- | --- | --- | --- |
| Oxygen | 10 bar/ 1,000 kPa | 0.2 kPa | 1 hour |
| Nitrous oxide | 10 bar/ 1,000 kPa | 0.2 kPa | 1 hour |
| Oxygen/nitrous oxide (50% v/v) | 10 bar/ 1,000 kPa | 0.2 kPa | 1 hour |
| Medical air 4 bar | 10 bar/ 1,000 kPa | 0.2 kPa | 1 hour |
| Surgical air 7 bar | 18 bar/ 1,800 kPa | 0.5 kPa | 1 hour |
| Surgical air 9 bar | 18 bar/ 1,800 kPa | 0.5 kPa | 1 hour |
| Medical vacuum | 5 bar/ 500 kPa | 0.2 kPa | 1 hour |
| Anaesthetic gas scavenging system (AGSS) | 70 kPa | 1 kPa | 15 mins |

### Labelling and marking, sleeving, supports and cross-connections

| Service | Labelling and markings | Sleeving and supports | Cross-connection test | Pass/ fail comments |
| --- | --- | --- | --- | --- |
| Oxygen | enter text | enter text | enter text | enter text |
| Nitrous oxide | enter text | enter text | enter text | enter text |
| Nitrous oxide/oxygen (50% v/v) mixture | enter text | enter text | enter text | enter text |
| Medical air 4 bar | enter text | enter text | enter text | enter text |
| Surgical air 7 bar | enter text | enter text | enter text | enter text |
| Medical vacuum* | enter text | enter text | enter text | enter text |
| AGSS | enter text | enter text | enter text | enter text |

Comments: enter text

## Part 2

The following pipeline systems interconnections have been made to facilitate the pipeline tests indicated in Part 1: enter text

## Part 3

The following pipeline systems interconnections have been removed as indicated in Part 2: enter text

## Sign off

This is to certify that the above tests have been carried out:

| Test undertaken by: | Name: | enter text | Signature: | enter text | Date: | enter a date |
| --- | --- | --- | --- | --- | --- | --- |
| Test witnessed by: | Name: | enter text | Signature: | enter text | Date: | enter a date |