# Medical gas quality tests - Form A21

| Healthcare organisation/ facility: | enter text | Date: | enter a date | Project ref: | enter text |
| --- | --- | --- | --- | --- | --- |

Quality specifications for medical gas pipeline tests (working gases). This is to certify that medical gas systems have been tested in accordance with Chapter 14 and Table 14.1.

## Medical gas quality tests

| Gas and Source | Particulate | Oil | Water | Carbon | Carbon dioxide | Nitrous and nitrous oxide | Sulphur dioxide | Poly-test tube (optional) | Odour | Pass/ fail |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Oxygen from bulk liquid or cylinders | Free from visible particles | N/A | ≤67 volume per million (vpm) (≤0.05 milligrams per litre (mg/l), dryer than -46oC dew point) | ≤5 milligrams per cubic metre (mg/m3) ≤5 parts per million (ppm) volume per volume (v/v) | ≤300 ppm v/v | N/A | N/A | No discolouration | No odour | pass/ fail |
| Nitrous oxide | Free from visible particles | N/A | ≤67 vpm (≤0.05 mg/l, dryer than -46oC dew point) | ≤5 mg/m3 ≤5 ppm v/v | ≤300 ppm v/v | ≤2 ppm v/v | N/A | No discolouration | Safety - not performed | pass/ fail |
| Oxygen/ nitrous oxide (50% v/v) mixture | Free from visible particles | N/A | ≤67 vpm (≤0.05 mg/l, dryer than -46oC dew point) | ≤5 mg/m3 ≤5 ppm v/v | ≤300 ppm v/v | ≤2 ppm v/v | N/A | No discolouration | Safety - not performed | pass/ fail |
| Medical and surgical air | Free from visible particles | ≤0.1 mg/m3 | ≤67 vpm (≤0.05 mg/l, dryer than -46oC dew point) | ≤5 mg/m3 ≤5 ppm v/v | ≤900 mg/m3 ≤500 ppm v/v | ≤2 ppm v/v | ≤1 ppm v/v | No discolouration | No odour | pass/ fail |
| Synthetic air | Free from visible particles | N/A | ≤67 vpm (≤0.05 mg/l, dryer than -46oC dew point) | N/A | N/A | N/A | N/A | No discolouration | No odour | pass/ fail |
| Oxygen from pressure swing adsorber (PSA) plant | Free from visible particles | ≤0.1 mg/m3 | ≤67 vpm (≤0.05 mg/l, dryer than -46oC dew point) | ≤5 mg/m3 ≤5 ppm v/v | ≤300 ppm v/v | ≤2 ppm v/v | ≤2 ppm v/v | No discolouration | No odour | pass/ fail |

## Sign off

This is to certify that the above tests have been carried out:

| Test undertaken by: | Name: | enter text | Signature: | enter text | Date: | enter a date |
| --- | --- | --- | --- | --- | --- | --- |
| Test witnessed by: | Name: | enter text | Signature: | enter text | Date: | enter a date |