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SHTM 02-01 Part A.15 - Form A15


Central alarm panel test - Form A15
	Healthcare organisation/ facility:
	enter text	Date:
	enter a date	Project ref:
	enter text

System details
	Alarm panel location: enter text

	Manufacturer/ model: enter text


Central alarm panel pressure settings
	Service
	SHTM 02 01 high-pressure setting (kilo Pascal (kPa))
	SHTM 02 01 low-pressure setting (kPa)
	Actual high-pressure setting (kPa)
	Actual low-pressure setting (kPa)

	Oxygen
	500
	385
	enter text	enter text
	Nitrous oxide
	500
	385
	enter text	enter text
	Oxygen/nitrous oxide (50% v/v) mixture
	500
	385
	enter text	enter text
	Medical air 4 bar (400 kPa)
	500
	385
	enter text	enter text
	Surgical air 7 bar (900 kPa)
	1,050
	800
	enter text	enter text
	Surgical air 7 bar (1,100 kPa)
	1,230
	1,050
	enter text	enter text
	Medical vacuum
	N/A
	360 millilmetres of mercury (mmHg)
	enter text	enter text

Central alarm panel tests	
	Service
	Test 1 ()
	Test 2 ()
	Test 3 ()
	Test 4 ()
	Test 5 ()
	Test 6 ()
	Test 7 ()
	Test 8 ()
	Test 9 ()
	Test 10 ()

	Oxygen
	☐	☐	☐	☐	☐	☐	☐	☐	☐	☐
	Nitrous oxide
	☐	☐	☐	☐	☐	☐	☐	☐	☐	☐
	Oxygen/nitrous oxide (50% v/v) mixture
	☐	☐	☐	☐	☐	☐	☐	☐	☐	☐
	Medical air 4 bar
	☐	☐	☐	☐	☐	☐	☐	☐	☐	☐
	Surgical air 7 bar
	☐	☐	☐	☐	☐	☐	☐	☐	☐	☐
	Medical vacuum
	☐	☐	☐	☐	☐	☐	☐	☐	☐	☐

List of tests
For central alarm panels, check that the operation of the mute switch cancels the audible alarm and converts the flashing signals to steady.
For repeater alarm panels, check that the mute switch cancels the audible only, and that the flashing signals are converted to steady via the central alarm panel.
For area alarm panels, check that the operation of the mute switch cancels the audible only.
Check power failure operates red system fault indicator and audible.
Check that a contact line fault operates the system fault indicator, the alarm indicator and the audible.
Check communication/wiring faults between central and repeater alarms operate the system fault indicator and audible.
Check audible reinstatement for each alarm panel.
Check that the audible can be continuously muted via operation of the internal push-button for gas service alarm condition only.
Check for correct identification of each gas service on alarm panels.
Depress test button and check that all lights are illuminated and the audible sounds.
Sign off
This is to certify that the above tests have been carried out:
	Test undertaken by:
	Name:
	enter text	Signature:
	enter text	Date:
	enter a date
	Test witnessed by:
	Name:
	enter text	Signature:
	enter text	Date:
	enter a date
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