# Central alarm panel test - Form A15

| Healthcare organisation/ facility: | enter text | Date: | enter a date | Project ref: | enter text |
| --- | --- | --- | --- | --- | --- |

## System details

Alarm panel location: enter text

Manufacturer/ model: enter text

## Central alarm panel pressure settings

| Service | SHTM 02 01 high-pressure setting (kilo Pascal (kPa)) | SHTM 02 01 low-pressure setting (kPa) | Actual high-pressure setting (kPa) | Actual low-pressure setting (kPa) |
| --- | --- | --- | --- | --- |
| Oxygen | 500 | 385 | enter text | enter text |
| Nitrous oxide | 500 | 385 | enter text | enter text |
| Oxygen/nitrous oxide (50% v/v) mixture | 500 | 385 | enter text | enter text |
| Medical air 4 bar (400 kPa) | 500 | 385 | enter text | enter text |
| Surgical air 7 bar (900 kPa) | 1,050 | 800 | enter text | enter text |
| Surgical air 7 bar (1,100 kPa) | 1,230 | 1,050 | enter text | enter text |
| Medical vacuum | N/A | 360 millilmetres of mercury (mmHg) | enter text | enter text |

## Central alarm panel tests

| Service | Test 1 () | Test 2 () | Test 3 () | Test 4 () | Test 5 () | Test 6 () | Test 7 () | Test 8 () | Test 9 () | Test 10 () |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Oxygen | ☐ | ☐ | ☐ | ☐ | ☐ | ☐ | ☐ | ☐ | ☐ | ☐ |
| Nitrous oxide | ☐ | ☐ | ☐ | ☐ | ☐ | ☐ | ☐ | ☐ | ☐ | ☐ |
| Oxygen/nitrous oxide (50% v/v) mixture | ☐ | ☐ | ☐ | ☐ | ☐ | ☐ | ☐ | ☐ | ☐ | ☐ |
| Medical air 4 bar | ☐ | ☐ | ☐ | ☐ | ☐ | ☐ | ☐ | ☐ | ☐ | ☐ |
| Surgical air 7 bar | ☐ | ☐ | ☐ | ☐ | ☐ | ☐ | ☐ | ☐ | ☐ | ☐ |
| Medical vacuum | ☐ | ☐ | ☐ | ☐ | ☐ | ☐ | ☐ | ☐ | ☐ | ☐ |

### List of tests

For central alarm panels, check that the operation of the mute switch cancels the audible alarm and converts the flashing signals to steady.

For repeater alarm panels, check that the mute switch cancels the audible only, and that the flashing signals are converted to steady via the central alarm panel.

For area alarm panels, check that the operation of the mute switch cancels the audible only.

Check power failure operates red system fault indicator and audible.

Check that a contact line fault operates the system fault indicator, the alarm indicator and the audible.

Check communication/wiring faults between central and repeater alarms operate the system fault indicator and audible.

Check audible reinstatement for each alarm panel.

Check that the audible can be continuously muted via operation of the internal push-button for gas service alarm condition only.

Check for correct identification of each gas service on alarm panels.

Depress test button and check that all lights are illuminated and the audible sounds.

## Sign off

This is to certify that the above tests have been carried out:

| Test undertaken by: | Name: | enter text | Signature: | enter text | Date: | enter a date |
| --- | --- | --- | --- | --- | --- | --- |
| Test witnessed by: | Name: | enter text | Signature: | enter text | Date: | enter a date |