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SHTM 02-01 Part A.13 - Form A13


Plant performance, operation and siting - Medical vacuum plant - Form A13
	Healthcare organisation/ facility:
	enter text	Date:
	enter a date	Project ref:
	enter text

System details
	Location: enter text

	Manufacturer/ model: enter text

	Type: Medical vacuum plant

	Function: choose a function

	Design flow: enter text

	Test flow: enter text





Medical vacuum plant settings
	Settings
	Plant setting millimetres of mercury (mmHg) kilo Pascal (kPa)
	Nominal pipeline pressure mmHg (kPa)
	Minimum design pressure at terminal unit mmHg (kPa)
	Minimum pressure at design flow mmHg (kPa)

	SHTM 02-01
	-500 to -660 mmHg
(66 – 88 kPa)
	450 mmHg
(60 kPa)
	400 mmHg
(55 kPa)
	300 mmHg
(40 kPa)

	Actual
	enter text
	N/A
	N/A
	enter text


Medical vacuum pump details
	Pump reference
	Type
	Serial no.
	Hours run
	Start (amps)
	Run (amps)
	Duty/ standby set point

	1
	enter text
	enter text
	enter text
	enter text
	enter text
	enter text

	2
	enter text
	enter text
	enter text
	enter text
	enter text
	enter text

	3
	enter text
	enter text
	enter text
	enter text
	enter text
	enter text

	4
	enter text
	enter text
	enter text
	enter text
	enter text
	enter text

	5
	enter text
	enter text
	enter text
	enter text
	enter text
	enter text

	6
	enter text
	enter text
	enter text
	enter text
	enter text
	enter text





Performance, operation and siting checklist
	Item
	Function/ operation
	Pass/ fail
	Comments

	1
	Power supplies provided
	pass/ fail	enter text
	2
	General operation
	pass/ fail	enter text
	3
	Leakage on joints
	pass/ fail	enter text
	4
	Excessive vibration and noise
	pass/ fail	enter text
	5
	Oil leakage
	pass/ fail	enter text
	6
	Earthing/ bonding
	pass/ fail	enter text
	7
	Correct sequence on start-up/ power failure
	pass/ fail	enter text
	8
	Plant indication - system functioning
	pass/ fail	enter text
	9
	Central alarm panel
	pass/ fail	enter text
	10
	Vacuum pump exhaust pipes discharge to a safe location
	pass/ fail	enter text
	11
	Plant room ventilation adequate
	pass/ fail	enter text
	12
	Plant room provided with hazard/ warning signs in accordance with Appendix E of SHTM 02-01 Part A
	pass/ fail	enter text
	13
	Access to and within plant room acceptable
	pass/ fail	enter text
	14
	Plantroom status (security, free from debris, obstructions and no unauthorised materials)
	pass/ fail	enter text
	15
	Plant room heating provided, type and method of control acceptable
	pass/ fail	enter text
	16
	Lighting provided (external/ internal)
	pass/ fail	enter text
	17
	Fire/ smoke detection and approved fire extinguisher
	pass/ fail	enter text
	18
	Piping and instrumentation diagram (P&ID) provided
	pass/ fail	enter text
	19
	Operating and maintenance manuals provided
	pass/ fail	enter text

Sign off
This is to certify that the above tests have been carried out:
	Test undertaken by:
	Name:
	enter text	Signature:
	enter text	Date:
	enter a date
	Test witnessed by:
	Name:
	enter text	Signature:
	enter text	Date:
	enter a date
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