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SHTM 02-01 Part A.11 - Form A11


Plant performance, operation and siting - Medical/ surgical air plant - Form A11
	Healthcare organisation/ facility:
	enter text	Date:
	enter a date	Project ref:
	enter text

System details
	Location: enter text

	Manufacturer/ model: enter text

	Type: choose an item if liquid cylinders: enter quantity

	Function: choose an item

	Design flow: enter text litres/min

	Test flow: enter text  litres/min

	Actual flow: enter text litres/min


Safety valve information
	Service valve (SV) reference
	Certificate reference
	Pressure setting kilo Pascal (kPa)

	
	
	

	SV1
	enter text	enter text
	SV2
	enter text	enter text
	SV3
	enter text	enter text
	SV4
	enter text	enter text

Performance, operation and siting checks - Medical/ surgical air plan
	Plant setting
	Plant regulator pressure setting (+/- 4%) (kPa)
	Nominal pipeline pressure (kPa)
	Minimum design pressure at terminal unit (kPa)
	Minimum pressure at design flow (kPa)

	SHTM 02-01 (4 bar)
	440
	420
	400
	380

	Actual (4 bar)
	enter text
	enter text
	N/A
	enter text

	SHTM 02-01 (7 bar)
	940
	900
	700
	700

	Actual (7 bar)
	enter text
	enter text
	N/A
	enter text



Compressor details
	Compressor reference
	Type
	Serial no.
	Hours run
	Start (amps)
	Run (amps)
	Pressure set point

	1
	enter text
	enter text
	enter text
	enter text
	enter text
	enter text

	2
	enter text
	enter text
	enter text
	enter text
	enter text
	enter text

	3
	enter text
	enter text
	enter text
	enter text
	enter text
	enter text

	4
	enter text
	enter text
	enter text
	enter text
	enter text
	enter text

	5
	enter text
	enter text
	enter text
	enter text
	enter text
	enter text

	6
	enter text
	enter text
	enter text
	enter text
	enter text
	enter text


Air receiver details
	Air receiver reference
	Type
	Serial no.

	1
	enter text
	enter text

	2
	enter text
	enter text

	3
	enter text
	enter text

	4
	enter text
	enter text

	5
	enter text
	enter text

	6
	enter text
	enter text


Performance, operation and siting checklist
	Item
	Function/ operation
	Pass/ fail
	Comments

	1
	Power supplies provided
	pass/ fail	enter text
	2
	General operation
	pass/ fail	enter text
	3
	Leakage on joints
	pass/ fail	enter text
	4
	Excessive vibration and noise
	pass/ fail	enter text
	5
	Oil leakage
	pass/ fail	enter text
	6
	Earthing/ bonding
	pass/ fail	enter text
	7
	Correct sequence on start-up/ power failure
	pass/ fail	enter text
	8
	Plant indication – system functioning
	pass/ fail	enter text
	9
	Central alarm panel
	pass/ fail	enter text
	10
	Safety valve exhaust pipes are separate and discharge to a safe location
	pass/ fail	enter text
	11
	Plant room ventilation adequate
	pass/ fail	enter text
	12
	Plant room provided with hazard/ warning signs in accordance with Appendix E of SHTM 02-01 Part A
	pass/ fail	enter text
	13
	Access to and within plant room acceptable
	pass/ fail	enter text
	14
	Plant room status (security, free from debris, obstructions and no unauthorised materials)
	pass/ fail	enter text
	15
	Plant room heating provided if specified, type and method of control acceptable
	pass/ fail	enter text
	16
	Lighting provided (external/ internal)
	pass/ fail	enter text
	17
	Fire/ smoke detection and approved fire extinguisher
	pass/ fail	enter text
	18
	Piping and instrumentation diagram (P&ID) provided
	pass/ fail	enter text
	19
	Operating and maintenance manuals provided
	pass/ fail	enter text
	20
	Condensate drain system provided, and drained via oil/ water separator to drain point
	pass/ fail	enter text
	21
	Emergency operating procedure and contact details
	pass/ fail	enter text

Sign off
This is to certify that the above tests have been carried out:
	Test undertaken by:
	Name:
	enter text	Signature:
	enter text	Date:
	enter a date
	Test witnessed by:
	Name:
	enter text	Signature:
	enter text	Date:
	enter a date
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