# Plant performance, operation and siting - Medical/ surgical air plant - Form A11

| Healthcare organisation/ facility: | enter text | Date: | enter a date | Project ref: | enter text |
| --- | --- | --- | --- | --- | --- |

## System details

Location: enter text

Manufacturer/ model: enter text

Type: choose an item if liquid cylinders: enter quantity

Function: choose an item

Design flow: enter text litres/min

Test flow: enter text litres/min

Actual flow: enter text litres/min

## Safety valve information

| Service valve (SV) reference | Certificate reference | Pressure setting kilo Pascal (kPa) |
| --- | --- | --- |
| SV1 | enter text | enter text |
| SV2 | enter text | enter text |
| SV3 | enter text | enter text |
| SV4 | enter text | enter text |

## Performance, operation and siting checks - Medical/ surgical air plan

| Plant setting | Plant regulator pressure setting (+/- 4%) (kPa) | Nominal pipeline pressure (kPa) | Minimum design pressure at terminal unit (kPa) | Minimum pressure at design flow (kPa) |
| --- | --- | --- | --- | --- |
| SHTM 02-01 (4 bar) | 440 | 420 | 400 | 380 |
| Actual (4 bar) | enter text | enter text | N/A | enter text |
| SHTM 02-01 (7 bar) | 940 | 900 | 700 | 700 |
| Actual (7 bar) | enter text | enter text | N/A | enter text |

### Compressor details

| Compressor reference | Type | Serial no. | Hours run | Start (amps) | Run (amps) | Pressure set point |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | enter text | enter text | enter text | enter text | enter text | enter text |
| 2 | enter text | enter text | enter text | enter text | enter text | enter text |
| 3 | enter text | enter text | enter text | enter text | enter text | enter text |
| 4 | enter text | enter text | enter text | enter text | enter text | enter text |
| 5 | enter text | enter text | enter text | enter text | enter text | enter text |
| 6 | enter text | enter text | enter text | enter text | enter text | enter text |

### Air receiver details

| Air receiver reference | Type | Serial no. |
| --- | --- | --- |
| 1 | enter text | enter text |
| 2 | enter text | enter text |
| 3 | enter text | enter text |
| 4 | enter text | enter text |
| 5 | enter text | enter text |
| 6 | enter text | enter text |

## Performance, operation and siting checklist

| Item | Function/ operation | Pass/ fail | Comments |
| --- | --- | --- | --- |
| 1 | Power supplies provided | pass/ fail | enter text |
| 2 | General operation | pass/ fail | enter text |
| 3 | Leakage on joints | pass/ fail | enter text |
| 4 | Excessive vibration and noise | pass/ fail | enter text |
| 5 | Oil leakage | pass/ fail | enter text |
| 6 | Earthing/ bonding | pass/ fail | enter text |
| 7 | Correct sequence on start-up/ power failure | pass/ fail | enter text |
| 8 | Plant indication – system functioning | pass/ fail | enter text |
| 9 | Central alarm panel | pass/ fail | enter text |
| 10 | Safety valve exhaust pipes are separate and discharge to a safe location | pass/ fail | enter text |
| 11 | Plant room ventilation adequate | pass/ fail | enter text |
| 12 | Plant room provided with hazard/ warning signs in accordance with Appendix E of SHTM 02-01 Part A | pass/ fail | enter text |
| 13 | Access to and within plant room acceptable | pass/ fail | enter text |
| 14 | Plant room status (security, free from debris, obstructions and no unauthorised materials) | pass/ fail | enter text |
| 15 | Plant room heating provided if specified, type and method of control acceptable | pass/ fail | enter text |
| 16 | Lighting provided (external/ internal) | pass/ fail | enter text |
| 17 | Fire/ smoke detection and approved fire extinguisher | pass/ fail | enter text |
| 18 | Piping and instrumentation diagram (P&ID) provided | pass/ fail | enter text |
| 19 | Operating and maintenance manuals provided | pass/ fail | enter text |
| 20 | Condensate drain system provided, and drained via oil/ water separator to drain point | pass/ fail | enter text |
| 21 | Emergency operating procedure and contact details | pass/ fail | enter text |

## Sign off

This is to certify that the above tests have been carried out:

| Test undertaken by: | Name: | enter text | Signature: | enter text | Date: | enter a date |
| --- | --- | --- | --- | --- | --- | --- |
| Test witnessed by: | Name: | enter text | Signature: | enter text | Date: | enter a date |