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SHTM 02-01 Part A.10 - Form A10


Plant performance, operation and siting - Medical gas manifold systems - Form A10
	Healthcare organisation/ facility:
	enter text	Date:
	enter a date	Project ref:
	enter text

System details
	Location: enter text

	Manufacturer/ model: enter text

	Gas service: choose an item If ‘other’ enter details here

	Function: choose an item

	Design flow: enter text litres/min

	Test flow: enter text litres/min

	Actual flow: enter text litres/min


Performance, operation and siting checks - Medical gas manifold systems
	Manifold type
	Left bank contents
	Right bank contents
	Quantity of cylinders per bank
	Cylinder type
	Duty bank

	Automatic changeover manifold (ACM)
	enter text bar
	enter text bar
	enter text
	enter text
	Choose an item
	Emergency reserve manifold (ERM)
	enter text bar
	enter text bar
	enter text
	enter text
	Choose an item

Pressure setting verification
	Settings
	Plant regulator pressure setting (+/- 4%) (kilo Pascal (kPa))
	Nominal pipeline pressure (kPa)
	Minimum design pressure at terminal unit (kPa)
	Minimum pressure at design flow (kPa)

	SHTM 02-01
	440
	420
	400
	380

	ACM
	enter text
	enter text
	enter text
	enter text

	ERM
	enter text
	enter text
	N/A
	N/A


Performance, operation and siting checklist
	Item
	Function/ operation
	Pass/ fail
	Comments

	1
	Power supplies provided
	pass/ fail	enter text
	2
	Leakage on joints
	pass/ fail	enter text
	3
	Heater operation (where applicable)
	pass/ fail	enter text
	4
	Operation of emergency manifold (where applicable)
	pass/ fail	enter text
	5
	Correct sequence on start-up/ power failure
	pass/ fail	enter text
	6
	Plant indication - system functioning
	pass/ fail	enter text
	7
	Central alarm panel
	pass/ fail	enter text
	8
	Safety valve exhaust pipes discharge to a safe location
	pass/ fail	enter text
	9
	Spare cylinder racks provided in accordance with the specification
	pass/ fail	enter text
	10
	Manifold room ventilation adequate
	pass/ fail	enter text
	11
	Manifold room provided with hazard/ warning signs in accordance with Appendix E of SHTM 02-01 Part A
	pass/ fail	enter text
	12
	Access to and within manifold room acceptable
	pass/ fail	enter text
	13
	Manifold room status (security, free from debris, obstructions and no unauthorised materials)
	pass/ fail	enter text
	14
	Manifold room heating provided, type and method of control to be noted
	pass/ fail	enter text
	15
	Lighting provided (external/ internal)
	pass/ fail	enter text
	16
	Fire/ smoke detection and approved fire extinguisher
	pass/ fail	enter text
	17
	Piping and instrumentation diagram (P&ID) provided
	pass/ fail	enter text
	18
	Operating and maintenance manuals provided
	pass/ fail	enter text
	19
	Cylinder identification chart
	pass/ fail	enter text
	20
	Manifold cylinder change procedure
	pass/ fail	enter text
	21
	Emergency manifold operating procedure and contact details
	pass/ fail	enter text

Safety valve information
	Safety valve (SV) reference
	Certificate reference
	Pressure setting (kPa)

	SV1
	enter text	enter text
	SV2
	enter text	enter text
	SV3
	enter text	enter text
	SV4
	enter text	enter text

Sign off
This is to certify that the above tests have been carried out:
	Test undertaken by:
	Name:
	enter text	Signature:
	enter text	Date:
	enter a date
	Test witnessed by:
	Name:
	enter text	Signature:
	enter text	Date:
	enter a date
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