# Plant performance, operation and siting - Medical gas manifold systems - Form A10

| Healthcare organisation/ facility: | enter text | Date: | enter a date | Project ref: | enter text |
| --- | --- | --- | --- | --- | --- |

## System details

Location: enter text

Manufacturer/ model: enter text

Gas service: choose an item If ‘other’ enter details here

Function: choose an item

Design flow: enter text litres/min

Test flow: enter text litres/min

Actual flow: enter text litres/min

## Performance, operation and siting checks - Medical gas manifold systems

| Manifold type | Left bank contents | Right bank contents | Quantity of cylinders per bank | Cylinder type | Duty bank |
| --- | --- | --- | --- | --- | --- |
| Automatic changeover manifold (ACM) | enter text bar | enter text bar | enter text | enter text | Choose an item |
| Emergency reserve manifold (ERM) | enter text bar | enter text bar | enter text | enter text | Choose an item |

## Pressure setting verification

| Settings | Plant regulator pressure setting (+/- 4%) (kilo Pascal (kPa)) | Nominal pipeline pressure (kPa) | Minimum design pressure at terminal unit (kPa) | Minimum pressure at design flow (kPa) |
| --- | --- | --- | --- | --- |
| SHTM 02-01 | 440 | 420 | 400 | 380 |
| ACM | enter text | enter text | enter text | enter text |
| ERM | enter text | enter text | N/A | N/A |

## Performance, operation and siting checklist

| Item | Function/ operation | Pass/ fail | Comments |
| --- | --- | --- | --- |
| 1 | Power supplies provided | pass/ fail | enter text |
| 2 | Leakage on joints | pass/ fail | enter text |
| 3 | Heater operation (where applicable) | pass/ fail | enter text |
| 4 | Operation of emergency manifold (where applicable) | pass/ fail | enter text |
| 5 | Correct sequence on start-up/ power failure | pass/ fail | enter text |
| 6 | Plant indication - system functioning | pass/ fail | enter text |
| 7 | Central alarm panel | pass/ fail | enter text |
| 8 | Safety valve exhaust pipes discharge to a safe location | pass/ fail | enter text |
| 9 | Spare cylinder racks provided in accordance with the specification | pass/ fail | enter text |
| 10 | Manifold room ventilation adequate | pass/ fail | enter text |
| 11 | Manifold room provided with hazard/ warning signs in accordance with Appendix E of SHTM 02-01 Part A | pass/ fail | enter text |
| 12 | Access to and within manifold room acceptable | pass/ fail | enter text |
| 13 | Manifold room status (security, free from debris, obstructions and no unauthorised materials) | pass/ fail | enter text |
| 14 | Manifold room heating provided, type and method of control to be noted | pass/ fail | enter text |
| 15 | Lighting provided (external/ internal) | pass/ fail | enter text |
| 16 | Fire/ smoke detection and approved fire extinguisher | pass/ fail | enter text |
| 17 | Piping and instrumentation diagram (P&ID) provided | pass/ fail | enter text |
| 18 | Operating and maintenance manuals provided | pass/ fail | enter text |
| 19 | Cylinder identification chart | pass/ fail | enter text |
| 20 | Manifold cylinder change procedure | pass/ fail | enter text |
| 21 | Emergency manifold operating procedure and contact details | pass/ fail | enter text |

### Safety valve information

| Safety valve (SV) reference | Certificate reference | Pressure setting (kPa) |
| --- | --- | --- |
| SV1 | enter text | enter text |
| SV2 | enter text | enter text |
| SV3 | enter text | enter text |
| SV4 | enter text | enter text |

## Sign off

This is to certify that the above tests have been carried out:

| Test undertaken by: | Name: | enter text | Signature: | enter text | Date: | enter a date |
| --- | --- | --- | --- | --- | --- | --- |
| Test witnessed by: | Name: | enter text | Signature: | enter text | Date: | enter a date |