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SHTM 02-01 Part A.09 - Form A9


Plant performance, operation and siting - Liquid oxygen systems - Form A9
	Healthcare organisation/ facility:
	enter text	Date:
	enter a date	Project ref:
	enter text

System details
	Location: enter text

	Manufacturer/ model: enter text

	Type: choose an item if liquid cylinders: enter quantity

	Function: choose an item

	Design flow: enter text litres/min

	Test flow: enter text  litres/min

	Primary tank pressure: enter text kilo Pascal (kPa)

	Secondary tank pressure: enter text kPa


Performance, operation and siting checks - Liquid oxygen	
	Service
	Plant regulator pressure setting (+/- 4%) (kPa)
	Nominal pipeline pressure (kPa)
	Minimum design pressure at terminal unit (TU) (kPa)
	Minimum pressure at design flow (kPa)

	
	
	
	
	

	Oxygen (SHTM 02-01)
	440
	420
	400
	380

	Oxygen (actual)
	enter text	enter text	enter text	enter text

Requirements for flow and pressure drop across terminal units with probes inserted
	TU nominal distribution pressure (kPa)
	Test pressure (kPa)
	Test flow (litres/min)
	Maximum pressure drop across a TU (kPa)

	
	
	
	

	400 to 500
	320
	40
	15

	400 to 500
	320
	200
	100

	700 to 1000
	560
	350
	100

	Vacuum
	-60
	25
	15



Performance, operation and siting checklist
	Item
	Function/ operation
	Pass/ fail
	Comments

	1
	Power supplies provided
	pass/ fail	enter text
	2
	General operation
	pass/ fail	enter text
	3
	Leakage on joints
	pass/ fail	enter text
	4
	Plant indication - system functioning
	pass/ fail	enter text
	5
	Earthing/ bonding
	pass/ fail	enter text
	6
	Central alarm panel
	pass/ fail	enter text
	7
	Safety valve exhaust pipes discharge to a safe location
	pass/ fail	enter text
	8
	Separation distances in compliance with Table 5.2 and British Compressed Gases Association (BCGA) CP36
	pass/ fail	enter text
	9
	Compound/ room provided with hazard/ warning signs in accordance with Appendix E of SHTM 02-01 Part A
	pass/ fail	enter text
	10
	Access and security to and within compound acceptable
	pass/ fail	enter text
	11
	Compound status (security, free from debris, obstructions and no unauthorised materials)
	pass/ fail	enter text
	12
	Lighting provided
	pass/ fail	enter text
	13
	Plant provided with all necessary valves and ancillaries
	pass/ fail	enter text
	14
	Spare cylinder racks for emergency reserve manifold (ERM)
	pass/ fail	enter text
	15
	Piping and instrumentation diagram (P&ID) provided
	pass/ fail	enter text
	16
	Operating and maintenance manuals provided
	pass/ fail	enter text
	17
	Emergency operating procedures and contact details
	pass/ fail	enter text



Sign off
This is to certify that the above tests have been carried out:
	Test undertaken by:
	Name:
	enter text	Signature:
	enter text	Date:
	enter a date
	Test witnessed by:
	Name:
	enter text	Signature:
	enter text	Date:
	enter a date
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