# Plant performance, operation and siting - Liquid oxygen systems - Form A9

| Healthcare organisation/ facility: | enter text | Date: | enter a date | Project ref: | enter text |
| --- | --- | --- | --- | --- | --- |

## System details

Location: enter text

Manufacturer/ model: enter text

Type: choose an item if liquid cylinders: enter quantity

Function: choose an item

Design flow: enter text litres/min

Test flow: enter text litres/min

Primary tank pressure: enter text kilo Pascal (kPa)

Secondary tank pressure: enter text kPa

## Performance, operation and siting checks - Liquid oxygen

| Service | Plant regulator pressure setting (+/- 4%) (kPa) | Nominal pipeline pressure (kPa) | Minimum design pressure at terminal unit (TU) (kPa) | Minimum pressure at design flow (kPa) |
| --- | --- | --- | --- | --- |
| Oxygen (SHTM 02-01) | 440 | 420 | 400 | 380 |
| Oxygen (actual) | enter text | enter text | enter text | enter text |

### Requirements for flow and pressure drop across terminal units with probes inserted

| TU nominal distribution pressure (kPa) | Test pressure (kPa) | Test flow (litres/min) | Maximum pressure drop across a TU (kPa) |
| --- | --- | --- | --- |
| 400 to 500 | 320 | 40 | 15 |
| 400 to 500 | 320 | 200 | 100 |
| 700 to 1000 | 560 | 350 | 100 |
| Vacuum | -60 | 25 | 15 |

## Performance, operation and siting checklist

| Item | Function/ operation | Pass/ fail | Comments |
| --- | --- | --- | --- |
| 1 | Power supplies provided | pass/ fail | enter text |
| 2 | General operation | pass/ fail | enter text |
| 3 | Leakage on joints | pass/ fail | enter text |
| 4 | Plant indication - system functioning | pass/ fail | enter text |
| 5 | Earthing/ bonding | pass/ fail | enter text |
| 6 | Central alarm panel | pass/ fail | enter text |
| 7 | Safety valve exhaust pipes discharge to a safe location | pass/ fail | enter text |
| 8 | Separation distances in compliance with Table 5.2 and British Compressed Gases Association (BCGA) CP36 | pass/ fail | enter text |
| 9 | Compound/ room provided with hazard/ warning signs in accordance with Appendix E of SHTM 02-01 Part A | pass/ fail | enter text |
| 10 | Access and security to and within compound acceptable | pass/ fail | enter text |
| 11 | Compound status (security, free from debris, obstructions and no unauthorised materials) | pass/ fail | enter text |
| 12 | Lighting provided | pass/ fail | enter text |
| 13 | Plant provided with all necessary valves and ancillaries | pass/ fail | enter text |
| 14 | Spare cylinder racks for emergency reserve manifold (ERM) | pass/ fail | enter text |
| 15 | Piping and instrumentation diagram (P&ID) provided | pass/ fail | enter text |
| 16 | Operating and maintenance manuals provided | pass/ fail | enter text |
| 17 | Emergency operating procedures and contact details | pass/ fail | enter text |

## Sign off

This is to certify that the above tests have been carried out:

| Test undertaken by: | Name: | enter text | Signature: | enter text | Date: | enter a date |
| --- | --- | --- | --- | --- | --- | --- |
| Test witnessed by: | Name: | enter text | Signature: | enter text | Date: | enter a date |