# Terminal unit functional tests exemplar - Form A8

| Healthcare organisation/ facility: | enter text | Date: | enter a date | Project ref: | enter text |
| --- | --- | --- | --- | --- | --- |

Area/ department: enter text

## Test parameters

| Service | Plant regulator pressure setting +/- 4 % | Nominal pipeline pressure | Minimum design pressure at terminal unit (TU) | Minimum pressure at design flow | Test flows (litres/min) |
| --- | --- | --- | --- | --- | --- |
| Oxygen | 440 kilo Pascal (kPa) | 420 kPa | 400 kPa | 380 kPa | 100 |
| Nitrous Oxide | 440 kPa | 420 kPa | 400 kPa | 380 kPa | 100 |
| Oxygen/nitrous oxide (50% v/v) mixture | 440 kPa | 420 kPa | 400 kPa | 380 kPa 310 kPa (275 litres/min) | 100 (other) 275 (Labour, delivery, recovery, postpartum (LDRP)) |
| Medical Air 4 Bar | 440 kPa | 420 kPa | 400 kPa | 380 kPa | 100 |
| Surgical Air 7 Bar Wall outlet | 860 kPa | 825 kPa | 784 kPa | 700 kPa | 350 |
| Surgical Air 7 Bar pendant hose | 940 kPa | 900 kPa | 854 kPa | 700 kPa | 350 |
| Medical Vacuum | 500 – 660 mmHg (66 – 88 kPa) | 450 mmHg (60 kPa) | 400 mmHg (55 kPa) | 300 mmHg (40 kPa) | 40 |

### Requirements for flow and pressure drop across terminal units with probes inserted

| TU nominal distribution pressure (kPa) | Test pressure (kPa) | Test flow (litres/min) | Maximum pressure drop across a TU (kPa) |
| --- | --- | --- | --- |
| 400 to 500 | 320 | 40 | 15 |
| 400 to 500 | 320 | 200 | 100 |
| 700 to 1000 | 560 | 350 | 100 |
| Vacuum | -60 | 25 | 15 |

## Terminal unit single point flowrates

| Service | Room no./ name | TU no. | Specified flow (litres/min) | Actual flow (litres/min) | Specified TU pressure drop (kPa) | Specified TU pressure drop achieved |
| --- | --- | --- | --- | --- | --- | --- |
| Oxygen | enter text | enter text | enter text | enter text | 15 | enter text |
| Nitrous oxide | enter text | enter text | enter text | enter text | 15 | enter text |
| Oxygen/nitrous oxide (50% v/v) mixture | enter text | enter text | enter text | enter text | 15 | enter text |
| Medical air 4 bar | enter text | enter text | enter text | enter text | 15 | enter text |
| Surgical air 7 bar | enter text | enter text | enter text | enter text | 70 | enter text |
| Medical vacuum | enter text | enter text | enter text | enter text | 15 | enter text |

## Terminal unit mechanical function tests

| Service | Room no./ name | TU no. | 1 | 2 | 3 | 4 | 5 | 6 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Oxygen | enter text | enter text | pass/ fail/ N/A | pass/ fail/ N/A | pass/ fail/ N/A | pass/ fail/ N/A | pass/ fail/ N/A | pass/ fail/ N/A |
| Nitrous oxide | enter text | enter text | pass/ fail/ N/A | pass/ fail/ N/A | pass/ fail/ N/A | pass/ fail/ N/A | pass/ fail/ N/A | pass/ fail/ N/A |
| Oxygen/nitrous oxide (50% v/v) mixture | enter text | enter text | pass/ fail/ N/A | pass/ fail/ N/A | pass/ fail/ N/A | pass/ fail/ N/A | pass/ fail/ N/A | pass/ fail/ N/A |
| Medical air 4 bar | enter text | enter text | pass/ fail/ N/A | pass/ fail/ N/A | pass/ fail/ N/A | pass/ fail/ N/A | pass/ fail/ N/A | pass/ fail/ N/A |
| Surgical air 7 bar | enter text | enter text | pass/ fail/ N/A | pass/ fail/ N/A | pass/ fail/ N/A | pass/ fail/ N/A | pass/ fail/ N/A | pass/ fail/ N/A |
| Medical vacuum | enter text | enter text | pass/ fail/ N/A | pass/ fail/ N/A | pass/ fail/ N/A | pass/ fail/ N/A | pass/ fail/ N/A | pass/ fail/ N/A |

Notes: The TU mechanical function tests are listed below:

- Mechanical function test to include, probe insertion, capture and release.

- The anti-swivel pin is present or absent dependent of orientation.

- The TU should be secured with all fixing screws.

- The TU facia (where fitted) or medical service module (bedhead trunking or pendant) cover plate should not restrict movement of the TU.

- The TU facia should be flush with the wall surface.

- Ensure the prohibition or ‘danger - do not use’ labels or tamperproof terminal unit (TU) blank plugs are provided.

## Sign off

This is to certify that the above tests have been carried out:

| Test undertaken by: | Name: | enter text | Signature: | enter text | Date: | enter a date |
| --- | --- | --- | --- | --- | --- | --- |
| Test witnessed by: | Name: | enter text | Signature: | enter text | Date: | enter a date |