# Pendant/ miscellaneous non-interchangeable screw thread (NIST) connectors - Specificity and function tests - Form A6

| Healthcare organisation/ facility: | enter text | Date: | enter a date | Project ref: | enter text |
| --- | --- | --- | --- | --- | --- |

Location: enter text

## Specificity and function tests

| Service | Quantity | NIST specificity pass/ fail | NIST function pass/ fail | Comments |
| --- | --- | --- | --- | --- |
| Oxygen | enter text | pass/ fail | pass/ fail | enter text |
| Nitrous oxide | enter text | pass/ fail | pass/ fail | enter text |
| Nitrous oxide/oxygen (50% v/v) mixture | enter text | pass/ fail | pass/ fail | enter text |
| Medical air 4 bar | enter text | pass/ fail | pass/ fail | enter text |
| Surgical air 7 bar | enter text | pass/ fail | pass/ fail | enter text |
| Medical vacuum | enter text | pass/ fail | N/A | enter text |

Notes:

- Ensure that the gas specific probes fully engage into the relevant gas specific NIST and that the probe can be secured.

- Ensure that the NIST allows flow of gas.

- Ensure that the NIST non-return valve (NRV) resets (with the exception of medical vacuum) to prevent flow of gas. In some instances a residual flow will occur, this depends on effective the NIST NRV is.

## Sign off

This is to certify that the above tests have been carried out:

| Test undertaken by: | Name: | enter text | Signature: | enter text | Date: | enter a date |
| --- | --- | --- | --- | --- | --- | --- |
| Test witnessed by: | Name: | enter text | Signature: | enter text | Date: | enter a date |