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SHTM 02-01 Part A.06 - Form A6


Pendant/ miscellaneous non-interchangeable screw thread (NIST) connectors - Specificity and function tests - Form A6
	Healthcare organisation/ facility:
	enter text	Date:
	enter a date	Project ref:
	enter text


	Location: enter text


Specificity and function tests
	Service
	Quantity
	NIST specificity pass/ fail
	NIST function pass/ fail
	Comments

	Oxygen
	enter text
	pass/ fail	pass/ fail	enter text

	Nitrous oxide
	enter text
	pass/ fail	pass/ fail	enter text

	Nitrous oxide/oxygen (50% v/v) mixture
	enter text
	pass/ fail	pass/ fail	enter text

	Medical air 4 bar
	enter text
	pass/ fail	pass/ fail	enter text

	Surgical air 7 bar
	enter text
	pass/ fail	pass/ fail	enter text

	Medical vacuum
	enter text
	pass/ fail	N/A
	enter text




Notes: 
1. Ensure that the gas specific probes fully engage into the relevant gas specific NIST and that the probe can be secured.
2. Ensure that the NIST allows flow of gas.
3. Ensure that the NIST non-return valve (NRV) resets (with the exception of medical vacuum) to prevent flow of gas. In some instances a residual flow will occur, this depends on effective the NIST NRV is.
Sign off
This is to certify that the above tests have been carried out:
	Test undertaken by:
	Name:
	enter text	Signature:
	enter text	Date:
	enter a date
	Test witnessed by:
	Name:
	enter text	Signature:
	enter text	Date:
	enter a date
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